## Rawdata
Type of Facility | A.2. Name of the District: | A.3. Name of the Block: | A.4. Name of the DH: | A.4. Name of the CHC/CH: | A.4. Name of the PHC: | A.5. Name of the Facility-In-Charge: | A.6. Facility-In-Charge Email-id: | A.7. Mobile number of Facility-In-Charge: | A.8. Name of the Monitor: | A.9. Date of visit: | 1. Fire Safety Assessment | 1.1. Are Fire extinguishers installed in the premises? | 1.2. Type of Fire Extinguisher: | 1.2.i. If Others, Please specify: | 1.2.1. If Dry Chemical Powder, number of fire extinguisher: | 1.2.1.1. If Dry Chemical Powder, is date of examination, date of refilling, status of pressure gauge(green or red) mentioned in all the fire extinguisher: | 1.2.2. If CO2 Carbon Dioxide, number of fire extinguisher: | 1.2.2.1. If CO2 Carbon Dioxide, is date of examination, date of refilling, status of pressure gauge(green or red) mentioned in all the fire extinguisher: | 1.2.3. If Water, number of fire extinguisher: | 1.2.3.1. If Water, is date of examination, date of refilling, status of pressure gauge(green or red) mentioned in all the fire extinguisher: | 1.2.4. If Foam, number of fire extinguisher: | 1.2.4.1. If Foam, is date of examination, date of refilling, status of pressure gauge(green or red) mentioned in all the fire extinguisher? | 1.2.5. If Wet Chemical, number of fire extinguisher: | 1.2.5.1. If Wet Chemical, Is date of examination, date of refilling, status of pressure gauge(green or red) mentioned in all the fire extinguisher: | 1.2.6. If Others, number of fire extinguisher: | 1.2.6.1. If Others, is date of examination, date of refilling, status of pressure gauge(green or red) mentioned in all the fire extinguisher? | 1.3. ls the inspection conducted periodically? | 1.3.1. Whether date of last inspection is mentioned in all fire extinguisher: | 1.4. Are all fire extinguisher in working condition? | 1.5. Are all fire extinguisher located at appropriate positions? | 1.6. Are instructions indicated on the extinguishers? | 1.7. Is the language of instruction understood by all employees? | 1.8. Are all fire extinguisher placed at appropriate height? | 1.9. Can all exit doors opened easily and quickly? | 1.9.1. If yes, type of emergency exit: | 1.9.1.i. If Others, please specify: | 1.9.1.1. If Main door, How many main doors exist: | 1.9.1.2. If Side door, How many side doors exist: | 1.9.1.3. If Others, How many other emergency door exist: | 1.10. Are fire doors free from obstruction? | 1.11. Are escape routes clear of obstructions? | 1.12. Are facility (resources) maps and escape route displayed in the premises? | 1.13. Fire Alarm available: | 1.13.1. If yes, all fire alarms are working properly: | 1.13.2. If yes, fire alarm panel working: | 1.14. Smoke detectors are available: | 1.14.1. If yes, all smoke detectors working properly: | 1.15. Whether fire hydrant available: | 1.15.1. If yes, number of Sand Buckets: | 1.15.2. If yes, number of Water Buckets: | 1.16. Whether hose reel available and appropriate to reach all parts of facility: | 1.17. ls facility of separate water tanker available in the premises? | 1.18. Motor pump working properly: | 1.19. Are luminaries and exit signs properly fixed in place? | 1.20. Are all fire extinguisher/firefighting equipment's accessible? | 1.21. Emergency plan available: | 1.22. ls emergency fire fighting training and SOP disseminated to the staff? | 1.22.1. If yes, how many staff knows to handle the equipment? | 1.23. Are do's and don'ts displayed at appropriate locations within premises? | 1.24. Are employees aware of emergency contact numbers? | 1.25. Are emergency contact numbers displayed inside the premises? | 1.27. Is the storage of diesel cans near to flammable scrap or electric system? | 1.28. Is there any safety wardens in-charge of fire safety among staff? | 1.28.1. Fire drill practise regularly: | 1.28.1.1. If yes, what is the interval of fire drill practice? | 1.28.1.2. If yes, date of last drill: | 1.29. Is the building Ventilating System maintained or inspected by the Registered Specialist Contractors (Ventilation Works) annually? | Remarks: | 2. Electrical Safety Assessment | 2.1. Is the central shutdown system in place? | 2.2. Has the Miniature Circuit Breaker (MCB) system installed? | 2.3. Are the wires coated with insulating material? | 2.4. Are the electric aisles removed before closing the facility? | 2.5. Are receptacles installed to cover live wires? | 2.6. Are electrical equipment's and wires checked and replaced at regular intervals? | 2.7. Are those equipment's, which get heated installed at least 1 meter away from any kind of highly combustible materials? | 2.8. ls the earthing properly done in the facility? | 2.8.1. If Yes, Earthing used(Plate/Pipe) is working? | 2.8.2. If Yes, Is Earthing voltage in healthy condition? | 2.9. Do the rooms have separate, dedicated power panels for both computer equipment and the A/C system? | 2.10. ls any defective equipment in use in the facility? | 2.10.1. If yes, please specify: | 2.11. Are there any live wires lying or tangled in the open? | 2.12. ls electricity tapped at any electrical joint? | 2.13. ls any plug point used for multiple loads? | 2.13.1. If Yes, how many points used for multiple loads? | 2.14. Whether the mentioned parameter are in healthy condition: | 2.14.1. Power supply switches and fuses/distribution panel: | 2.14.1.1. Take a photo of main board: | 2.14.2. In general, what is your assessment of the input voltage? | 2.14.2.1. If others, please specify: | 2.14.3. All Power Points- switches, sockets: | 2.14.4. All Electrical Connection/Joints: | 2.14.5. Power Cable fixed: | 2.14.6. MCBs, ELCB: | 2.14.6.i. Are MCB/ELCB are separate for different rooms? | 2.14.7. Are all important equipment's attached with a Stabilizer and in working condition? | 2.14.8. Rubber mat near electrical panel: | 2.14.9. All the electrical circuits properly plugged and grounded? | 2.14.10. Output voltage from main electrical panels: | 2.15. Whether fire extinguisher available? | 2.16. Is the use of extension cords prohibited? | 2.17. Are electrical panels and branch circuit disconnects freely accessible at all times? | 2.18. Is electrical equipment in wet areas, such as laundry rooms, kitchens, bathrooms, and out of doors, equipped with ground fault protection and designed for wet conditions? | 2.19. Is electrical equipment inspected and maintained according to manufacturer's instructions? | 2.20. Are electrical cords and connections for appliances inspected before use? | Remarks:
DH | BALODA BAJAR |  | DH Baloda Bazar |  |  | Dr.Abhay Kumar parihar | csbalodabazar...3@gmail.com,cmhobalodabazar@gmail.com,rmnchadurg@gmail. com | 9425202648 | Dr.Rashmi bhonsle | 27-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Poor |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No | Yes | Yes | 1 |  | Yes | 1482762550090.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | No | Yes | Yes | Fair
CHC or CH | BALODA BAJAR | BALODABAZAAR |  | CHC Lavan |  | Dr. K. L. Banjare | rmncha2balod@gmail.com,nhmbalodabazar@gmail.com,chclawan2016@gmail.com | 9977618307 | No one here | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | No | [10 empty] | Yes | No | Yes | Yes | No | Yes | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | Yes | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | No | No |  |  | Yes | 1482818892213.jpg | Constant |  | No | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | No | No | No | No
CHC or CH | BALODA BAJAR | BHATAPARA |  | CH Bhatapara |  | Dr.Rajesh awasthi | chcbhatapara. 07726@gmail.com,nhmbalodabazar@gmail. com,rmnchadurg@gmail. com | 9425518144 | Dr.Rashmi bhonsle | 25-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | No |  | Yes | Yes | Yes | No | Yes | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | Yes | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Poor |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No |  | No | No | Yes | 1 |  | Yes | 1482646093751.jpg | Constant |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Fair
CHC or CH | BALODA BAJAR | BILAIGARH |  | CHC Bilaigarh |  | Dr.Suresh Khute | bmobilaigarh01@gmail.com, cmhobb2012@gmail.com, nrhmbalodabazar@gmail.com, rmnchabalodabazar321@gmail.com, rmncha2durg@gmail.com | 9981672428 | Dr.Suresh Khute | 31-12-2016 |  | No | [21 empty] | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No arrangement for fire safety |  | Yes | No | Yes | No | No | No | No | Yes | Yes | No | Yes | No |  | Yes | No | No |  |  | No |  | Constant |  | No | No | Yes | No |  | Yes | No | Yes | Yes | No | No | No | No | No | No | No Arrangements for fire protection
CHC or CH | BALODA BAJAR | KASDOL |  | CHC Kasdol |  | Dr. C. S. Paikara | chckasdol@rediffmail.com,nhmbalodabazar@gmail.com,rmncha2balod@gmail.com | 9755984146 | Mr. Chandram | 28-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Don't know |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No | No |  |  | Yes | 1482836894284.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes
CHC or CH | BALODA BAJAR | PALARI |  | CHC Palari |  | Dr.F.R.Nirala | bmopallari11@gmail.com, cmhobb2012@gmail.com, nrhmbalodabazar@gmail.com, rmncha2durg@gmail.com, rmnchabalodabazar321@gmail.com | 9977888846 | Dr.F.R. Nirala | 31-12-2016 |  | Yes | Foam | [7 empty] | 4 | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 3 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | Yes | 12 | No | No | No | No | Yes | Yes | Quarterly | 2016-09-06 | Yes | Good Arrangements for fire fighting |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No | No |  |  | Yes | 1482584103293.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Electrical Connections are in Good Condition
CHC or CH | BALODA BAJAR | SIMGA |  | CHC Simga |  | Dr.P.L.Chandan | bmosimga@gmail.com,nhmbalodabazar@gmail.com,cmhobb2012@gmail.com | 9926886342 | Dr.Rashmi bhonsle | 25-12-2016 |  | Yes | CO2 Carbon Dioxide |  |  |  | 2 | No | [8 empty] | No |  | Yes | Yes | Yes | No | Yes | Yes | Main door |  | 4 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Poor |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes | No | Yes | 1 |  | Yes | 1482565595923.jpg | Constant |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Fair
DH | BALRAMPUR |  | DH Balrampur |  |  | Dr. R. K. Tripathi | csbalrampur@gmail.com, rmnchasurguja@gmail.com | 7354121121 | Mona Arora | 23-12-2016 |  | No | [21 empty] | Yes | Main door |  | 2 |  |  | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | Yes | 12 | No | No | No | No | No |  |  |  | No | . |  | No | No | No | No | No | No | No | Yes | Yes | No | No | No |  | No | No | No |  |  | Yes | 1482400098974.jpg | Constant |  | Yes | Yes | Yes | No |  | Yes | No | Yes | Yes | No | No | Yes | No | No | Yes | ..
PHC | BASTAR | BAKAVAND |  |  | PHC Karpawand | RMA Roshan Nirmalkar | phckarpawand@gmail.com,bbbbakawand@gmail.com,rmnchakanker@gmail.com | 9589554778 | Dr vikas katare | 25-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Not aware |  | Yes | Yes | Yes | No | No | No | No | No |  |  | No | Yes | Cooler | Yes | Yes | Yes | 2 |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | Yes | No | No | No | No | No | No | No | No | Awareness training IEC required
PHC | BASTAR | BAKAVAND |  |  | PHC Kolawal | RMA RAJNISH SHUKLA | bbbbakawand@gmail.com,dpm.bastar@gmail.com,rmnchakanker@gmail.com | 9926297891 | Dr vikas katare | 25-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 2 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | Yes | No | No | No | No |  |  |  | No | Staff aware but training required |  | Yes | Yes | Yes | Yes | Yes | No | No | No |  |  | No | No |  | No | No | No |  |  | Yes | 1482679339540.jpg | Consistently low voltage |  | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | No | Yes | No | No | No | Staff aware but training required
PHC | BASTAR | BAKAVAND |  |  | PHC Jaibel | Mrs. Tama Gain | bbbbakawand@gmail.com, phcjaibel@gmail.com, rmnchadhamtari@gmail.com | 7587134445 | Dr. Vijendra Kumar Kashyap | 26-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | No | [10 empty] | No |  | Yes | No | Yes | No | Yes | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No fire safety measures & precautions/preparations is there |  | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  | No | No | Yes | 2 |  | Yes | 1482726584400.jpg | Constant |  | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | No | Yes | No | No | No | Proper evaluation and maintenance must be there
PHC | BASTAR | BAKAVAND |  |  | PHC Malgaon | Mrs. Arpita Singh | bbbbakawand@gmail.com | 9425596876 | Dr. Vijendra Kumar Kashyap | 26-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | No | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 2 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Fire safety measures must be there |  | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | No | Yes | 2 |  | No |  | Constant |  | No | No | No | Yes | No | No | No | No | Yes | Yes | No | No | Yes | No | No | Electrical safety measures must be there
CHC or CH | BASTAR | BASTANAAR |  | CHC Badekilepal |  | Dr Pradeep baghel | bbbkilepal@gmail.com,rmnchasukma1@gmail.com | 9425596184 | Dr Gulshan carpenter | 26-12-2016 |  | Yes | Dry Chemical Powder |  | 3 | No | [10 empty] | No |  | Yes | No | Yes | Yes | Yes | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Staff not trained on fire extinguisher operations |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | Yes | 2 |  | Yes | 1482752295434.jpg | Consistently low voltage |  | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | No | No | No | No | No | Main door is used for entrance & exit
PHC | BASTAR | BASTANAAR |  |  | PHC Bade Kaklur | Mr Shailendra Kumar sonkala RMA | bbbkilepal@gmail.com | 7587182488 | Dr.Gulshan carpenter | 26-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | No | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | No | [5 empty] | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No training given during installation of fire extinguisher |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | Yes | 1482760785627.jpg | Consistently low voltage |  | Yes | No | Yes | Yes | No | No | No | No | Yes | Yes | No | No | No | No | No | No electricity supply , only solar power is available.
PHC | BASTAR | BASTANAAR |  |  | PHC Mutanpal | Mr Abhishek Mishra RMA | bbbkilepal@gmail.com,rmnchasukma1@gmail.com | 9009540909 | Dr Gulshan carpenter | 26-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Staff not aware about fire safety measure . |  | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | Yes | 3 |  | No |  | Others | Voltage fluctuations | No | No | No | No |  | No | No | No | No | No | No | No | No | No | No | No Electricity supply , Complete dependency on solar
PHC | BASTAR | BASTAR |  |  | PHC Rotma | Sree Kumar joshi | dpm.bastar@gmail.com,rmnchakanker@gmail.com | 9479177257 | DPM vikas katare | 25-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | Yes | [10 empty] | No |  | Yes | Yes | Yes | No | Yes | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Staff training required |  | Yes | Yes | Yes | No | Yes | No | No | No |  |  | No | No |  | No | No | No |  |  | No |  | Others | Light connection not there | No | No | No | No |  | No | Yes | No | No | Yes | No | No | No | No | No | Training required
PHC | BASTAR | BASTAR |  |  | PHC Ghotia | RMA SAVITRI MADARIYA | dpm.bastar@gmail.com,rmnchakanker@gmail.com | 9406410203 | Dr vikas katare | 25-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Not even know |  | Yes | Yes | Yes | No | No | No | No | No |  |  | No | No |  | No | No | No |  |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | Yes | No | No | No | No | No | No | No | No | Not aware training required
PHC | BASTAR | BASTAR |  |  | PHC Mudagaon | Mr. Deepak Kshatriya | dpm.bastar@gmail.com, rmnchadhamtari@gmail.com | 9826834740 | Dr. Vijendra Kumar Kashyap | 26-12-2016 |  | Yes | Dry Chemical Powder, Others | Sand | 2 | No | [8 empty] | 6 | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Fire safety measures, precautions as well as emergency preparations must be there |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  | No | No | Yes | 1 |  | Yes | 1482772154112.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Electrical safety measures must be there
CHC or CH | BASTAR | BASTAR |  | CH Bhanpuri |  | Dr b d roy | dpm.bastar@gmail.com,rmnchakanker@gmail.com | 9630305182 | Dr vikas katare | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 8 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | Yes | No | No |  |  |  | No | Staff training required |  | Yes | Yes | Yes | No | Yes | No | Yes | No |  |  | No | Yes | ILR portables xray machine | Yes | Yes | Yes | 2 |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | Yes | No | No | Yes | No | No | No | No | No | Staff training required
PHC | BASTAR | BASTAR |  |  | PHC Kesharpal | Dr p c thakur | dpm.bastar@gmail.com,rmnchakanker@gmail.com | 9407773884 | Dr vikas katare | 27-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Only one room |  | No | No | No | No | No | No | No | No |  |  | No | No |  | No | No | No |  |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | No | No | No | No | No | No | No | No | No | Electric line not installed
PHC | BASTAR | BASTAR |  |  | PHC Kesharpal | RMA HEMANT BARSANGDE | dpm.bastar@gmailcom,rmnchakanker@gmail.com | 9424162937 | Dr vikas katare | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Training required |  | Yes | Yes | Yes | No | No | No | Yes | No |  |  | No | No |  | Yes | Yes | No |  |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | Yes | No | No | Yes | No | No | No | No | No | Staff Not aware
PHC | BASTAR | DARBHA |  |  | PHC Kukanar | Mr. Nitesh gupta RMA | bmochindgarh@gmail.com,rmnchasukma@gmail.com | 9424167343 | Dr.Gulshan carpenter | 26-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No fire extinguisher installed, single gate used for entrance & exit. |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | Yes | 2 |  | Yes | 1482600516502.jpg | Others | Voltage not constant | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | No | No | Fire extinguisher not installed , staff is not aware about fire safety precautions.
CHC or CH | BASTAR | DARBHA |  | CHC Darbha |  | Dr P.L Mandavi | bbbdarbha2@gmail.com,rmnchasukma1@gmail.com | 9424108534 | Dr Gulshan carpenter | 26-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | Yes | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Fire extinguisher not installed , no seperate exit doors |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | No |  | Yes | Yes | Yes | 2 |  | No |  | Others | Voltage fluctuations are there | No | No | No | No |  | Yes | No | No | No | No | No | No | Yes | No | No | No fire extinguisher installed.
PHC | BASTAR | DARBHA |  |  | PHC Pakhnar | Mr Dinesh sinha RMA | bbbdarbha@gmail.com,rmnchasukma1@gmail.com | 7587331001 | Dr Gulshan carpenter | 27-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | No | Yes | No | No | No | Yes | Yes | Yes | No | No | No |  | Yes | Yes | Yes | 2 |  | Yes | 1482839259105.jpg | Consistently low voltage |  | No | No | No | No |  | No | No | No | No | No | No | No | No | No | No | No power supply in facility
PHC | BASTAR | DARBHA |  |  | PHC Sautnar | Mr. Surendra kumar sahu | bbbdarbha@gmail.com,bmochhindgarh@gmail.com,rmnchasukma1@gmail.com | 9424210420 | Dr Gulshan carpenter | 30-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 1 |  |  | No | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No electrify supply , only solar backup available, entrance & exit gate are same. |  | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | No | No |  | Yes | No | Yes | 2 |  | Yes | 1482827615686.jpg | Consistently low voltage |  | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | No | No | No | No | No fire extinguisher installed
CHC or CH | BASTAR | LOHANDIGUDA |  | CHC Lohandiguda |  | Dr. N K Nag | lohandiguda@gmail.com, dpm.bastar@gmail.com, rmnchadhamtari@gmail.com | 9406077774 | Dr. Vijendra Kumar Kashyap | 28-12-2016 |  | Yes | Dry Chemical Powder, CO2 Carbon Dioxide |  | 1 | No | 1 | No | [8 empty] | No |  | No | No | Yes | No | No | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Fire safety measures must be there |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  | No | No | Yes | 3 |  | Yes | 1482857693795.jpg | Constant |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | No | No | Electrical safety measures & precautions must be there
PHC | BASTAR | LOHANDIGUDA |  |  | PHC Alnar | Mr. Amit Kumar Mishra | lohandiguda@gmail.com, dpm.bastar@gmail.com | 9406076194 | Dr. Vijendra Kumar Kashyap | 28-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | No | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | Yes | 1 | No | No | No | No | No |  |  |  | No | Fire safety assessment must be done at regular intervals |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  | No | No | Yes | 1 |  | Yes | 1482934372160.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | All staff must be aware of electrical safety measures
PHC | BASTAR | LOHANDIGUDA |  |  | PHC Binta | Mrs. Premsheela Panigrahi | lohandiguda@gmail.com | 7587005479 | Dr. Vijendra Kumar Kashyap | 30-12-2016 |  | No | [21 empty] | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Fire safety assessment must be done at regular intervals |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | ILR not working properly | No | No | No |  |  | Yes | 1483070481653.jpg | Consistently low voltage |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Electrical safety measures must be there
PHC | BASTAR | NANGOOR |  |  | PHC Adawal | RMA Mahesh Mishra | phcadawal@gmail.com,rmnchakanker@gmail.com | 9926144802 | Dr vikas katare | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | Yes | [10 empty] | No |  | Yes | No | Yes | Yes | No | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Poor, not aware |  | Yes | Yes | Yes | No | No | No | Yes | No |  |  | No | No |  | Yes | Yes | Yes | 3 |  | No |  | Others | Fluctuations | No | No | No | No |  | No | Yes | No | No | Yes | No | No | No | No | No | Need training and equipment
PHC | BASTAR | NANGOOR |  |  | PHC Nagarnar | RMA VIKAS DAS | dpm.bastar@gmail.com,rmnchakanker@gmail.com | 8700915608 | Dr vikas katare | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | No | [10 empty] | No |  | Yes | No | Yes | No | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Very poor |  | Yes | Yes | Yes | No | No | No | Yes | No |  |  | No | No |  | Yes | Yes | Yes | 2 |  | No |  | Others | Fluctuations | No | No | No | No |  | No | No | No | No | Yes | No | Yes | No | No | No | Need training and equipment
PHC | BASTAR | NANGOOR |  |  | PHC Kurandi | Mr. Mithlesh Chandra RMA | rmnchasukma1@gmail.com,dr.mithilesh1008@gmail.com | 9770103059 | Dr Gulshan carpenter | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | Yes | [10 empty] | No |  | Yes | Yes | Yes | No | No | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Training , awareness on fire safety required for staff. |  | Yes | No | Yes | No | Yes | No | No | No |  |  | No | No |  | No | No | Yes | 2 |  | Yes | 1482486465926.jpg | Consistently low voltage |  | No | No | No | No |  | No | No | No | No | Yes | No | No | No | No | No | Old building , no fire exit available , single door used for entry and exit.
CHC or CH | BASTAR | NANGOOR |  | CHC Nangoor |  | Dr.K S Saithe | bbbnangoor@gmail.com,rmnchasukma1@gmail.com | 07772926786 | Dr Gulshan carpenter | 23-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | Yes | 4 | No | No | No | No | No |  |  |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | Yes | 3 |  | Yes | 1482494053023.jpg | Consistently low voltage |  | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | No | No | No | Training not given to staff during installation of fire extinguisher.
PHC | BASTAR | TOKOPAAL |  |  | PHC Kalepal | Mrs. Abha Shahi | bbbtokapal@gmail.com, dpm.bastar@gmail.com, rmnchadhamtari@gmail.com | 9713279202 | Dr. Vijendra Kumar Kashyap | 27-12-2016 |  | No | [21 empty] | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Fire & electrical safety measures must be there |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  | No | No | Yes | 2 |  | Yes | 1482778272305.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | No | No | Regular checkups & maintenance must have to be done
PHC | BASTAR | TOKOPAAL |  |  | PHC Ransargipal | Mr. Mithlesh Shahi | dpm.bastar@gmail.com, rmnchadhamtari@gmail.com | 9826143633 | Dr. Vijendra Kumar Kashyap | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | No | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Fire safety measures must be there |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  | No | No | Yes | 1 |  | Yes | 1482807548684.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Regularly electrical assessment as well as routine checkups must be done
CHC or CH | BASTAR | TOKOPAAL |  | CHC Tokapal |  | Dr sarita mahobiya bmo | dpm.bastar@gmail.com,rmnchakanker@gmail.com | 9424281759 | Dr vikas katare | 28-12-2016 |  | Yes | Dry Chemical Powder |  | 6 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door |  | 2 | 2 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | Yes | No | No | No | No |  |  |  | No | Staff training required |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | No | No |  | No | No | No |  |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | Yes | No | No | Yes | No | No | No | No | No | Staff training required
PHC | BASTAR | TOKOPAAL |  |  | PHC Mawlibhata | RMA sarita sahare | dpm.bastar@gmail.com,rmnchakanker@gmail.com | 9479161550 | Dr vikas katare | 28-12-2016 |  | Yes | Dry Chemical Powder |  | 3 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Staff training required |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | No | No |  | No | Yes | No |  |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | Yes | No | No | Yes | No | Yes | No | No | No | Staff training required
DH | BEMETRA |  | DH Bemetara |  |  | Dr v k srivastav | Csdhbemetara@gmail.com | 9424107218 | Bhupendra bari | 24-12-2016 |  | Yes | CO2 Carbon Dioxide |  |  |  | 8 | No | [8 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door |  | 5 | 2 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | No | No | No |  |  |  | No | Vendor should come and visit regularly |  | Yes | Yes | Yes | No | Yes | Yes | No | No |  |  | Yes | No |  | No | Yes | Yes | 15 |  | Yes | 1482490332974.jpg | Constant |  | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Poor maintenance
PHC | BEMETRA | BERLA |  |  | PHC Devrbija | Mr. Praveen Sapre | bemetaracmho@yahoo.com, ddo.nrhmbemetara@gmail.com, dpmbemetara027@gmail.com | 9669006868 | Mr. Praveen Sapre | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 2961 | Yes | [10 empty] | No |  | Yes | Yes | Yes | No | Yes | Yes | Side door |  |  | 1 |  | Yes | Yes | Yes | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | No | Yes | No | No | No | Yes | No |  |  | No | No |  | No | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
PHC | BEMETRA | NAWAGARH |  |  | PHC Sambalpur | M k jaiswal | Sambalpurphc@ | 9907703155 | Ajay lehre | 24-12-2016 |  | No | [21 empty] | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | Yes | 1 | No | No | No | No | No |  |  |  | Yes | No visit done by vendors |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No |  | No | No | Yes | 3 |  | Yes | 1482571355661.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Less awareness
CHC or CH | BEMETRA | SAJA |  | CH Saja |  | Dr. S.N.Jangde | bmosaja@gmail.com | 9926615535 | Abhishek shukla | 24-12-2016 |  | Yes | Dry Chemical Powder |  | 29192 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 1 |  |  | Yes | Yes | Yes | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Not monitored |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | Yes | 1482565235735.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Not done regularly
PHC | DURG | DHAMDHA |  |  | PHC Surdung | Dr. Trivendra Mishra | phcsurdung4@rediffmail.com | 7489368415 | Takeshwar ram nishad | 22-12-2016 |  | Yes | Dry Chemical Powder |  | 32631 | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door |  | 1 | 1 |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Not monitored |  | No | No | Yes | No | No | Yes | Yes | Yes | No | Yes | No | No |  | No | Yes | No |  |  | Yes | 1482399558687.jpg | Constant |  | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Not maintained properly
PHC | DURG | DURG |  |  | PHC Kohaka | Dr. Pushpaanju | phc_kohka@yahoo.com | 9826189550 | Omeshwari sahu | 20-12-2016 |  | Yes | Dry Chemical Powder |  | 6397 | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [5 empty] | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | Yes | Only installed, but no information available and records are also absent. |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | Yes | No |  |  | Yes | 1482232787914.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Good as it is new building.
PHC | DURG | PATAN |  |  | PHC Batrel | Priyanka shiv kumar | phcbatrel@gmail.com,cmodurg@yahoo.com | 9826234878 | Dayaram sahu | 21-12-2016 |  | Yes | Dry Chemical Powder |  | 5992 | Yes | [10 empty] | No |  | No | Yes | No | Yes | Yes | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No |  | Yes | No | No | No | No |  |  |  | No | Not maintained |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | Yes | 1482311953539.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Not maintained
CHC or CH | GARIYABAND | FINGESHWAR |  | CHC Fingeshwar |  | Dr..p.kudeshia | bmo_chcfingeshwar@yahoo.com,rmnchadurg@gmail.com | 9893878707 | Dr.Rashmi bhonsle | 18-12-2016 |  | Yes | Foam | [7 empty] | 2 | No |  |  |  |  | No |  | Yes | Yes | Yes | No | Yes | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Poor |  | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | Yes | 1481961547914.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Fair
CHC or CH | JANJGIR CHAMPA | AKALTARA |  | CH Bdm Champa |  | Dr. Anita srivastava | bdmchampa@gmail.com, cmhojanjgir@gmail, rmnchamahasamund@gmail | 9826074515 | Sandeep chandrakar | 19-12-2016 |  | No | [21 empty] | Yes | Side door |  |  | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | Yes | No | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | No | Yes | No | No | No | Yes | No |  |  | Yes | No |  | Yes | Yes | Yes | 6 |  | Yes | 1481962237782.jpg | Constant |  | No | Yes | No | No |  | No | No | No | No | No | No | No | Yes | No | No | No specific electrical safety assessment
PHC | JANJGIR CHAMPA | BAMHANIDIH |  |  | PHC Darang | Mr. Bhupendra patle | bmobamhanidih@rediffmail | 9329179333 | Sandeep chandrakar | 19-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No fire safety system installed in PHC. No specific plan |  | No | No | Yes | No | No | No | No | No |  |  | No | No |  | Yes | No | Yes | 2 |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | No | No | No | No | No | No | No | No | No | No specific method used
PHC | JANJGIR CHAMPA | DABHARA |  |  | PHC Devarghata | Mr. Arvind Kumar khunte | deverghata.phc@rediffmail.com, bmodabhara@rediffmail.com, cmhojanjgir@gmail.com, rmnchamahasamund@gmail. com | 9617441636 | Sandeep chandrakar | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | No | [10 empty] | No |  | No | Yes | No | No | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | Yes | Yes | No | No | No | No | No |  |  | No | No |  | Yes | Yes | Yes | 2 |  | No |  | Constant |  | No | No | No | Yes | Yes | No | No | No | No | Yes | No | No | No | No | No | No specific electrical safety management
PHC | JANJGIR CHAMPA | DABHARA |  |  | PHC Tundri | Mr. Patnaik | bmodabhara@rediffmail.com, cmhojanjgir@gmail.com, rmnchamahasamund@gmail. com | 9770522702 | Sandeep chandrakar | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | No | [10 empty] | No |  | Yes | Yes | No | No | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | No |  | No | No | No |  |  | Yes | 1482517061030.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | No | No | No | No | No | No specific electrical safety management
CHC or CH | JANJGIR CHAMPA | DABHARA |  | CHC Dabhara |  | Dr. N P mishra | bmodabhara@rediffmail.com, cmhojanjgir@gmail.com, rmnchamahasamund@gmail.com | 9329409691 | Sandeep chandrakar | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 5 | No | [10 empty] | No |  | Yes | Yes | No | No | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | Yes | Yes | No | No | No | No | No |  |  | No | No |  | Yes | Yes | Yes | 3 |  | No |  | Constant |  | No | No | No | Yes | Yes | No | No | No | No | Yes | No | No | No | No | No | No specific electrical safety management
PHC | JANJGIR CHAMPA | JAIJAIPUR |  |  | PHC Thathari | Mr. Khilawan das kurre | phc_thathari@rediffmail.com | 9827732636 | Sandeep chandrakar | 19-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | No | [10 empty] | No |  | Yes | Yes | Yes | No | No | Yes | Main door, Side door |  | 1 | 1 |  | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | No |  | No | No | No |  |  | Yes | 1482135824653.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | No | Yes | No | No | No specific electrical safety management
PHC | JANJGIR CHAMPA | JAIJAIPUR |  |  | PHC Hasaud | Mr. Yogendra sahu | bmojaijaipur@rediffmail, cmhojanjgir@gmail, rmnchamahasamund@gmail | 8817183989 | Sandeep chandrakar | 19-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | No | [10 empty] | No |  | Yes | Yes | Yes | No | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | Yes | Yes | No | No | No | No | No |  |  | No | No |  | Yes | Yes | No |  |  | Yes | 1482143576445.jpg | Constant |  | No | No | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | No | No | No | No | No specific electrical safety management
CHC or CH | JANJGIR CHAMPA | JAIJAIPUR |  | CHC Jaijaipur |  | Dr. S l banjare | bmojaijaipur@rediffmail, cmhojanjgir@gmail, rmnchamahasamund@gmail | 9993685007 | Sandeep chandrakar | 20-12-2016 |  | Yes | Dry Chemical Powder |  | 6 | Yes | [10 empty] | No |  | Yes | Yes | Yes | No | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | No | Yes | No | No | Yes | No | No |  |  | Yes | No |  | Yes | Yes | Yes | 3 |  | Yes | 1482217595480.jpg | Constant |  | No | No | Yes | No |  | No | No | No | No | Yes | No | No | No | No | Yes | No specific electrical safety management
PHC | JANJGIR CHAMPA | MAALKHARAUD |  |  | PHC Pirada | Mr. Tileshwar prasad | bmomalkharoda@rediffmail.com, cmhojanjgir@gmail, rmnchamahasamund@gmail | 7898960091 | Sandeep chandrakar | 20-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | No | Yes | No | Yes | No | Yes | No |  |  | No | No |  | Yes | Yes | No |  |  | No |  | Constant |  | No | No | No | No |  | No | No | No | No | No | No | No | No | No | No | No specific electrical safety management
PHC | JANJGIR CHAMPA | MAALKHARAUD |  |  | PHC Ghoghari | Dr. Katyayani singh | bmomalkharoda@rediffmail com, cmhojanjgir@gmail, rmnchamahasamund@gmail | 7770832992 | Sandeep chandrakar | 20-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | No |  | Constant |  | Yes | No | Yes | Yes | Yes | No | No | Yes | No | No | No | No | No | No | No | No specific electrical safety management
PHC | JANJGIR CHAMPA | MAALKHARAUD |  |  | PHC Adhbhar | Mr. Dhanesh sahu | rmaadbhar@gmail.com, bmomalkharoda@rediffmail. com, cmhojanjgir@gmail.com, rmnchamahasamund@gmail.com | 9009953770 | Sandeep chandrakar | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | No |  | Yes | Yes | No |  |  | Yes | 1482301987618.jpg | Constant |  | Yes | Yes | No | Yes | Yes | No | No | No | No | No | No | No | No | No | No | No specific electrical safety management
PHC | JANJGIR CHAMPA | MAALKHARAUD |  |  | PHC Faguram | Mr. Rajkumar gabel | bmomalkharoda@rediffmail.com, cmhojanjgir@gmail.com, rmnchamahasamund@gmail.com | 7773021623 | Sandeep chandrakar | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | No | No | No | No | No | No | No | No |  |  | No | No |  | Yes | Yes | Yes | 3 |  | No |  | Constant |  | No | No | No | No |  | No | No | No | No | No | No | No | No | No | No | No specific electrical safety management.
CHC or CH | JANJGIR CHAMPA | MAALKHARAUD |  | CHC Malkharoda |  | Dr. K L uraon | bmomalkharoda@rediffmail.com, cmhojanjgir@gmail.com, rmnchamahasamund@gmail.com | 9424161488 | Sandeep chandrakar | 21-12-2016 |  | Yes | Dry Chemical Powder |  | 3 | No | [10 empty] | No |  | Yes | Yes | No | No | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No specific fire safety management |  | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | No |  |  | Yes | 1482316617263.jpg | Constant |  | No | No | Yes | Yes | Yes | No | No | No | No | Yes | No | No | No | No | No | No specific electrical safety management
PHC | KAWARDHA | BODLA |  |  | PHC Baijalpur | Aanchal Hathile (RMA) | mr.sss2012@rediffmail.com | 9993743743 | Aanchal Hathile | 17-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No | Ventilation not in any rooms |  | No | Yes | No | No | No | No | Yes | No |  |  | No | No |  | No | Yes | Yes | 7 |  | Yes | 1481949953254.jpg | Constant |  | No | No | No | Yes | No | No | No | Yes | Yes | No | No | Yes | No | Yes | No
PHC | KAWARDHA | BODLA |  |  | PHC Taregaon | Mr. Tribhuwan shingroli | ravishankar12689@gmail.com | 7389033720 | Mr. Tribhuwan Singhroli | 17-12-2016 |  | No | [21 empty] | No | [5 empty] | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | Yes | Yes | No | No | No |  |  |  | No | No ventilater here. |  | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | Yes | 10 |  | No |  | Constant |  | Yes | Yes | Yes | No |  | No | No | No | No | No | Yes | No | No | No | No
PHC | KAWARDHA | BODLA |  |  | PHC Pondi | Mrs. Shraddha Chandrawanshi (RMA) | hemant28889@gmail.com | 9977885126 | Mrs. Shraddha Chandrawanshi | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | Yes | No | No | No |  |  |  | No | No proper ventilation |  | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | Yes | 2 |  | Yes | 1482335483144.jpg | Constant |  | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | No | Yes | No | No
CHC or CH | KAWARDHA | KAWARDHA |  | CHC Pipariya |  | Dr. Devendra kishor Belchandan | nrhm_bodla@rediffgmail.com | 9425564742 | Dr. Devendra kishor Belchandan | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No |  |  | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | Yes | 5 |  | Yes | 1482335989844.jpg | Constant |  | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | No | Yes | No | No
CHC or CH | KAWARDHA | KAWARDHA |  | CHC Pipariya |  | Dr. Satish Chandrawanshi | bpm13pipariya@gmail.com | 9752616768 | Dr. Satish Chandrawanshi | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | Yes | Yes | No | No | No |  |  |  | No | No ventilation |  | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | Yes | 1482335024591.jpg | Constant |  | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | No | Yes | No | Yes
PHC | KAWARDHA | PANDARIYA |  |  | PHC Dullapur | Mr. Ramchandra Patre | phcdullapur@mail.com | 7224922569 | Mr. Ramchandra Patre | 15-12-2016 |  | No | [21 empty] | Yes | Main door |  | 2 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | Yes | Yes | No | No | No |  |  |  | No | Ventilation is not proper in all rooms not inspected |  | No | No | No | Yes | No | No | Yes | No |  |  | No | No |  | Yes | Yes | Yes | 4 |  | No |  | Consistently high voltage |  | Yes | Yes | Yes | No |  | No | No | No | No | No | No | No | No | No | No | No meter is here, direct electricity here from the electric pole wire.
PHC | KAWARDHA | PANDARIYA |  |  | PHC Chirpani | Mr. Krishna Kumar jaiswal (RMA) | chhirpaniphc@gmail.com | 9981237290 | Mr. Krishna Kumar jaiswal (RMA) | 15-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No |  |  | No | Yes | No | No | No | No | Yes | No |  |  | No | No |  | No | Yes | No |  |  | No |  | Constant |  | No | No | Yes | Yes | No | No | No | No | No | No | Yes | No | No | No | Yes
PHC | KAWARDHA | PANDARIYA |  |  | PHC Kishungarh | Mr. Yogesh chandrawanshi (RMA) | phckishungarh@gmail.com | 9479055031 | Mr. Yogesh chandrawanshi (RMA) | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | Yes | Yes | Yes | No | No |  |  |  | No |  |  | No | Yes | No | Yes | No | No | No | Yes | Yes | No | No | No |  | Yes | Yes | No |  |  | Yes | 1482311382061.jpg | Constant |  | No | No | No | No |  | Yes | No | No | No | No | No | No | No | Yes | Yes
PHC | KAWARDHA | PANDARIYA |  |  | PHC Kukdur | Dr. B. L. Raj | phckukdur2016@gmail.com | 8304910747 | Dr. B. L. Raj | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | Yes | No |  | No | Yes | No | No | No |  |  |  | No |  |  | No | Yes | No | No | No | No | No | Yes | Yes | Yes | No | No |  | No | Yes | Yes | 3 |  | No |  | Constant |  | Yes | Yes | Yes | Yes | No | No | No | No | Yes | No | No | No | Yes | No | No
CHC or CH | KAWARDHA | SAHASPUR LOHARA |  | CHC Slohara |  | Dr. Arjun Singh Thakur | nrhm_slohara@rediffmail.com | 9981330302 | Dr. Arjun Singh Thakur | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | Yes | No | No |  |  |  | No | Ventilation not in proper manner and no inspection there. |  | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | Yes | 1482311970853.jpg | Constant |  | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | Yes | No | Yes | Yes | Inspected
PHC | KAWARDHA | SAHASPUR LOHARA |  |  | PHC Bhimbhori | Mr. R. G. Yadu (RMA) | phcbhimbhouri@gmail.com | 7879390079 | Mr. R. G. Yadu | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | Yes | Yes | No | No | No |  |  |  | No | Ventilation not in proper manner |  | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | Yes | 1482334052081.jpg | Constant |  | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | Yes | Yes | No | No | Not inspected
PHC | KAWARDHA | SAHASPUR LOHARA |  |  | PHC Rakse | Mr. Madan Singh | phc.rakshe@gmail.com | 9981843318 | Mr. Madam Singh | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | Yes | Yes | No | No | No |  |  |  | No | Ventilation not in proper manner |  | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | Yes | 1482334630762.jpg | Constant |  | Yes | Yes | No | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | No
DH | KONDAGAON |  | DH Kondagaon |  |  | Dr S P waare | bbbkondagaon@gmail.com,cskondagaon@gmail.com,dpm.kondagaon@gmail.com | 9826179405 | Dr S P Waare | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 16 | Yes | [10 empty] | No |  | Yes | Yes | Yes | No | No | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Need training of staff regularly,designated personal needed |  | Yes | Yes | No | No | No | No | No | No |  |  | No | Yes | AC, FREEZ,COMPUTER,EXTRNTIONS | Yes | No | Yes | 6 |  | Yes | 1482291645604.jpg | Consistently low voltage |  | No | No | No | No |  | No | No | No | No | Yes | No | No | No | No | No | Poor management of equipment s
CHC or CH | KONDAGAON | KESHKAL |  | CHC Keshkal |  | Dr. H K Baghel | bbbkeshkal@gmail.com, dpm.kondagaon@gmail.com | 9752719678 | Dr. Vijendra Kumar Kashyap | 30-12-2016 |  | Yes | Dry Chemical Powder |  | 2 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door, Others | Small back door behind labour room | 2 | 1 | 1 | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Fire safety measures must be there |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  | No | No | Yes | 4 |  | Yes | 1483072222782.jpg | Constant |  | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Electrical safety measures must be there for hospital as well as staff
PHC | KONDAGAON | KONDAGAON |  |  | PHC Bunagaon | Smt Shweta Devangan RMA | bbbkondagaon@gmail.com,rmnchasukma1@gmail.com,dpmkondagaon@gmail.com | 7587805558 | Dr Gulshan Carpenter | 30-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | No |  | No | No | Yes | 2 |  | Yes | 1482909187973.jpg | Others | Fluctuate some times | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | No | No | Electric wiring done properly & underground , but staff not aware about fire safety measures , no for extinguisher installed.
PHC | KONDAGAON | KONDAGAON |  |  | PHC Dahikonga | Mr Shashikala poyam | bbbkondagaon@gmail.com,rmnchasukma1@gmail.com,dpmkondagaon@gmail.com | 9425598725 | Dr.Gulshan carpenter | 30-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | No documentation done for fire safety |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  | No | Yes | Yes | 3 |  | Yes | 1482903563153.jpg | Consistently low voltage |  | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | No | Yes | Yes | No | No | Wires lying in facility connecting one room to other.
CHC or CH | KONDAGAON | PHARASGAON |  | CHC Pharasgaon |  | Dr Lakhan jurri | bbbpharasgaon@gmail.com,dpm.kondagaon@gmail.com,rmnchakanker@gmail.com | 9981237888 | Dr vikas katare | 30-12-2016 |  | Yes | Dry Chemical Powder |  | 4 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door |  | 3 | 2 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Staff training required |  | Yes | Yes | Yes | No | No | No | Yes | No |  |  | No | No |  | Yes | Yes | Yes | 2 |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | Yes | Yes | No | Yes | No | Yes | No | No | No | Staff training required
DH | MUNGELI |  | DH Mungeli |  |  | Dr RK Bhuarya | csmungeli@gmail.com | 9425532599 | Aakash Sharma | 25-12-2016 |  | Yes | Dry Chemical Powder |  | 5 | Yes | [10 empty] | No |  | Yes | Yes | Yes | No | Yes | Yes | Main door, Side door |  | 1 | 4 |  | Yes | Yes | Yes | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Not proper measures |  | Yes | Yes | Yes | No | No | No | No | No |  |  | Yes | Yes | Radiant warmer, bsu. | Yes | Yes | No |  |  | Yes | 1482633823249.jpg | Consistently low voltage |  | No | No | No | Yes | No | No | No | No | Yes | Yes | No | Yes | No | No | No | Circuits are not proper
PHC | MUNGELI | LORMI |  |  | PHC Khairwar Khurd | Shrawan kumar Jaiswal | No id | 9993633663 | Aakash Sharma | 24-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | No | [10 empty] | No |  | Yes | Yes | Yes | No | Yes | Yes | Main door, Side door |  | 1 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No |  |  | No | Yes | Yes | No | Yes | No | No | No |  |  | No | No |  | No | Yes | Yes | 2 |  | Yes | 1482633290966.jpg | Constant |  | No | No | Yes | No |  | No | No | No | Yes | Yes | No | Yes | No | No | No | Poor
PHC | MUNGELI | LORMI |  |  | PHC Semarsal | Mr. Balram Chandrakar | bpmulormi@gmail.com, cmhomungeli@gmail.com | 7089670060 | Mr. Balram Chandrakar | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 2 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  | No |  |  | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | Yes | 1482845460991.jpg | Constant |  | No | No | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes
PHC | MUNGELI | LORMI |  |  | PHC Khudiya | Mr. Satpal kanwar | bpmulormi@gmail, cmhomungeli@gmail.com | 8719083096 | Mr. Satpal kanwar | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | No | No | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | Yes | 2 |  | No |  | Constant |  | No | No | No | No |  | No | No | Yes | Yes | Yes | No | No | Yes | No | Yes
CHC or CH | MUNGELI | LORMI |  | CHC Lormi |  | Dr. G. S. Dau | dpmulormi@gmail.com | 8304910747 | Dr. G. S. Dau | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 3 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | Yes | No | No |  |  |  | No |  |  | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | Yes | 1482848127314.jpg | Constant |  | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
PHC | MUNGELI | MUNGELI |  |  | PHC Jarhagaun | Mrs. Nilima Rathor | cmhomungeli@gmail.com | 9300238284 | Mrs. Nilima Rathor | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Main door |  | 2 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | Yes | Yes | No | No | No |  |  |  | No |  |  | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | Yes | 3 |  | No |  | Constant |  | No | No | Yes | Yes | No | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes
PHC | MUNGELI | MUNGELI |  |  | PHC Khamariya | Mr. D. L. Sahu (pharmacist) | cmhomungeli@gmail.com | 9754094204 | Mr. T. R. S. Parihar (Pharmacist) | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | No |  | No | No | Yes | No | Yes | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No |  |  | No | No | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | Yes | 2 |  | Yes | 1482846383452.jpg | Constant |  | Yes | Yes | No | No |  | No | No | Yes | Yes | Yes | No | No | Yes | No | Yes
PHC | MUNGELI | MUNGELI |  |  | PHC Setganga | Dr. Sanjay Oberoy | cmhomungeligmail.com | 9300068909 | Dr. Sanjay Oberoy | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | Yes | No |  | No | Yes | Yes | No | No |  |  |  | No |  |  | No | No | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | Yes | 3 |  | Yes | 1482846857204.jpg | Constant |  | Yes | Yes | No | No |  | No | No | No | Yes | Yes | No | No | Yes | No | No
CHC or CH | MUNGELI | PATHARIYA |  | CHC Pathariya |  | Dr. A. Banjare | cmhomungeli@gmail.com | 9425564369 | Dr. A. Banjare | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | Yes | No | No |  |  |  | No |  |  | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | No |  | Constant |  | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes
PHC | MUNGELI | PATHARIYA |  |  | PHC Amora | Mr. Kamlesh Pali | cmhomungeli@gmail.com | 9926155021 | Mr. Kamlesh Pali | 27-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No |  |  | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No | Yes | Yes | 2 |  | No |  | Constant |  | Yes | Yes | Yes | No |  | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes
PHC | MUNGELI | PATHARIYA |  |  | PHC Rambode | Mrs. Sumita Tandan (RMA) | cmhomungeli@gmail.com | 9098430394 | Mrs Sunita Tandan | 28-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No |  |  | No | No | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | No | Yes | No |  |  | No |  | Constant |  | Yes | No | Yes | No |  | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
PHC | MUNGELI | PATHARIYA |  |  | PHC Sildaha | Mr. Niraj ghritlahare | cmhomungeli@gmail.com | 9993351437 | Mr. Niraj Ghritlahre | 28-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | No |  | Yes | No | Yes | No | No | Yes | Main door |  | 1 |  |  | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | No | No | Yes | No | No | No | No | Yes | Yes | Yes | No | No |  | No | Yes | Yes | 2 |  | No |  | Consistently low voltage |  | No | Yes | No | No |  | No | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes
CHC or CH | MUNGELI | PATHARIYA |  | CHC Sargaon |  | Dr. Kamlesh khairwal | cmhomungeli@gmail.com, bpmupatharia@gmail.com | 8965054437 | Dr. Kamlesh khairwal | 28-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | Yes | [10 empty] | No |  | Yes | No | Yes | No | Yes | Yes | Main door, Side door |  | 2 | 2 |  | No | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | Yes | No |  | No | Yes | Yes | No | No |  |  |  | No |  |  | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No | No | No |  |  | Yes | 1482905753657.jpg | Constant |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes
DH | NARAYANPUR |  | DH Narayanpur |  |  | Dr.V K Lohiya | csnarayanpur@gmail.com,rmnchasukma1@gmail.com | 9407909462 | Dr Gulshan carpenter | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 10 | Yes | [10 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Main door, Side door, Others | Back doors | 3 | 2 | 2 | Yes | Yes | No | No |  |  | No |  | No |  |  | No | Yes | Yes | No | Yes | No | Yes | 20 | No | Yes | Yes | No | No |  |  |  | No | Fire extinguishers are installed very well , only documentation with periodic inspection and sign board of does & don't required. |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fridge & OT Light | Yes | Yes | Yes | 4 |  | Yes | 1482462231668.jpg | Others | Periodically fluctuate | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Over all condition was good
PHC | NARAYANPUR | NARAYANPUR |  |  | PHC Benur | RMA N K JAIN | cmho.narayanpur@gmail.com | 9406235815 | RMA N K jain | 23-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Equipments required,Awareness and training required |  | Yes | Yes | Yes | No | No | No | Yes | No |  |  | Yes | Yes | Tubelight,cooler,tv | Yes | Yes | Yes | 2 |  | Yes | 1482406624157.jpg | Others | Fluctuations in voltage | No | No | No | No |  | No | No | No | No | No | No | No | No | No | No | Very poor
PHC | NARAYANPUR | NARAYANPUR |  |  | PHC Chhote Dongar | Mr ala ram dhruv RMA | cmho.narayanpur@gmail.com,rmnchasukma1@gmail.com | 9479267604 | Dr Gulshan Carpenter | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 6 | Yes | [10 empty] | No |  | Yes | Yes | Yes | Yes | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Needs awareness & Training , and documentation. |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  | Yes | No | Yes | 2 |  | No |  | Others | Voltage is not constant , fluctuate periodically. | No | No | No | Yes | Yes | No | No | No | No | Yes | No | Yes | No | No | No | Documentation , training and awareness of staff required with replacement of some switch boards.
PHC | NARAYANPUR | NARAYANPUR |  |  | PHC Dhanora | Avinash sakhardande | cmho.narayanpur@gmail.com | 9424278411 | Dr vikas katare | 23-12-2016 |  | Yes | Dry Chemical Powder |  | 1 | No | [10 empty] | No |  | Yes | No | Yes | No | No | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Poor arrangements |  | No | Yes | Yes | No | No | No | Yes | No |  |  | No | No |  | Yes | Yes | Yes | 1 |  | No |  | Consistently low voltage |  | No | No | No | No |  | No | No | No | No | Yes | No | Yes | No | No | No | Not aware training required
CHC or CH | NARAYANPUR | ORCHHA |  | CHC Orchha |  | Dr. B N Bhanpuriya | dpm.narayanpur@gmail.com, rmnchadhamtari@gmail.com | 9425598179 | Dr. Vijendra Kumar Kashyap | 24-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Fire safety measures, procedures as well as staff orientation must be in place. |  | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | Yes | No | Yes | 3 |  | Yes | 1482550615139.jpg | Constant |  | No | No | Yes | No |  | No | No | No | Yes | No | Yes | Yes | Yes | No | No | Regular maintenance, repair & monitoring must be in place
PHC | RAIGARH | BARAMKELA |  |  | PHC Saria | Mukesh Chowdhari | phcsariya@gmail.com | 8085913344 | Dr Husna Paravin | 18-12-2016 |  | Yes | Dry Chemical Powder |  | 7336371 | Yes | [10 empty] | No |  | No | Yes | Yes | No | Yes | No | [5 empty] | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | Yes | Yes | No | No |  | No | No | No | No | No |  |  |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No |  | No | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | Yes
CHC or CH | RAIGARH | BARAMKELA |  | CHC Baramkela |  | Dr Awdesh Panigrahi | bpmubaramkela@gmail.com | 9425275247 | Dr Husna Paravin | 28-12-2016 |  | No | [21 empty] | Yes | Side door |  |  | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | No |  | No | No | Yes | 3 |  | Yes | 1482941190636.jpg | Constant |  | No | No | No | Yes | Yes | Yes | No | No | No | No | No | No | No | No | Yes
PHC | RAIGARH | BARAMKELA |  |  | PHC Lendhra | Saurabh Agrawal | phclendhra1999@gmail.com | 9893166991 | Dr Husna Paravin | 28-12-2016 |  | Yes | Dry Chemical Powder |  | 7336371 | Yes | [10 empty] | No |  | No | No | Yes | No | No | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No |  | Yes | No | Yes | 3 |  | Yes | 1482941717844.jpg | Constant |  | No | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | No
PHC | RAIGARH | BARAMKELA |  |  | PHC Dongripali | Dr T L Mishra | Phcdongripali@gmail.com | 9669522323 | Husna Paravin | 28-12-2016 |  | No | [21 empty] | Yes | Main door, Others | Back door | 1 |  | 1 | Yes | Yes | Yes | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | Yes | No | No | No | No | No | Yes | No | No | No | No |  | Yes | No | Yes | 2 |  | Yes | 1482942009715.jpg | Constant |  | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | No | No | No | Yes
PHC | RAIGARH | PUSSORE |  |  | PHC Kondatarai | Raj kamal Patel | phckondatarai@gmail.com | 9407793991 | Dr Husna Paravin | 18-12-2016 |  | Yes | Dry Chemical Powder |  | 7753387 | No | [10 empty] | No |  | No | Yes | Yes | No | Yes | Yes | Side door |  |  | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | No |  | Constant |  | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes
CHC or CH | RAIGARH | PUSSORE |  | CHC Pussore |  | Dr B K Chandravanshi | bpmupussore@gmail.com | 9827400376 | Dr Husna Paravin | 18-12-2016 |  | No | [21 empty] | No | [5 empty] | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | No | Yes | Yes | No | No | No | No | No |  |  | No | No |  | No | No | Yes | 2 |  | Yes | 1481967199089.jpg | Constant |  | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | Yes
PHC | RAIGARH | PUSSORE |  |  | PHC Badebhandar | Vimlesh Kaser | phcbadebhandar@gmail.com | 9755485186 | Husna Paravin | 24-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | No | No | No | No | No | No | No |  |  | No | No |  | No | No | Yes | 3 |  | Yes | 1482566221177.jpg | Constant |  | No | No | Yes | No |  | Yes | No | No | Yes | No | No | No | No | Yes | Yes
PHC | RAIGARH | PUSSORE |  |  | PHC Putkapuri | Uddhav Patel | Phphcputkapuri@gmail.com | 9993030650 | Dr Husna Paravin | 24-12-2016 |  | Yes | Dry Chemical Powder |  | 7753387 | Yes | [10 empty] | No |  | Yes | No | Yes | No | No | Yes | Others | Back door |  |  | 1 | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | No | No | No | No | No | No | Yes | No | No | No | No |  | Yes | No | Yes | 3 |  | No |  | Constant |  | No | No | Yes | No |  | Yes | No | No | No | No | No | Yes | No | No | Yes
PHC | RAIGARH | RAIGARH |  |  | PHC Bangusiya | Vidyadhar Chauhan | phcbangursia@gmail.com | 8817915246 | Husna Paravin | 26-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | No |  | No | No | Yes | 2 |  | Yes | 1482759908527.jpg | Constant |  | No | No | Yes | Yes | Yes | No | No | No | Yes | No | No | Yes | No | No | Yes
PHC | RAIGARH | TAMANAR |  |  | PHC Urba | O P kurre | phcurba@gmail.com | 9300931767 | Husna Paravin | 30-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | Yes | Yes | Yes | Yes | No | No | No | No |  |  | No | No |  | No | No | Yes | 3 |  | Yes | 1483059736936.jpg | Constant |  | No | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | No | Yes
DH | RAIPUR |  | DH Raipur |  |  | Dr. T. K. Agrawal | civilsurgeon.rpr@gmail.com,cmho_raipur@gmail.com,rmncha2@gmail.com | 7389911606 | Mr. Karan Tiwari | 21-12-2016 |  | Yes | Dry Chemical Powder |  | 12 | No | [10 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | Yes | 50 | No | No | No | No | Yes | No |  |  | No | No |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No | No | No |  |  | Yes | 1482214056861.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Check
CHC or CH | RAIPUR | ABHANPUR |  | CHC Abhanpur |  | Dr.amita jha | bmoabhanpur@gmail.com,nrhmraipur@yahoo.com,rmnchadurg@gmail.com | 9407922150 | Dr.rashmi bhonsle | 20-12-2016 |  | Yes | Foam | [7 empty] | 2 | Yes |  |  |  |  | No |  | Yes | Yes | Yes | No | Yes | Yes | Side door |  |  | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Poor |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes | No | No |  |  | No |  | Constant |  | Yes | Yes | No | Yes | No | Yes | No | No | Yes | Yes | No | Yes | No | No | Yes | Poor
CHC or CH | RAIPUR | ABHANPUR |  | CHC Nawapara |  | Dr.C.V.Gupta | rmncha2durg@gmail.com, cmho_raipur@yahoo.co.in, chcnawapara.mo@gmail.com | 9826516580 | Dr.C. V. Gupta | 31-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No arrangements regarding fire safety |  | No | Yes | Yes | No | Yes | No | Yes | No |  |  | No | No |  | No | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No | No | No | No arrangements regarding fire prevention
CHC or CH | RAIPUR | ARANG |  | CHC Arang |  | Dr.k.s.rai | bpmuarang@gmail.com,nrhmraipur@yahoo. com,rmnchadurg@gmail.com | 9424210361 | Dr.Rashmi bhonsle | 20-12-2016 |  | Yes | Foam | [7 empty] | 2 | Yes |  |  |  |  | No |  | Yes | No | Yes | No | No | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Poor |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | Yes | 1 |  | Yes | 1482222174046.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Fair
CHC or CH | RAIPUR | DHARSEEVA |  | CH Mana |  | Dr.gokul sarkar | Civilhospitalmanacamp@gmail.com,cmho_raipur@yahoo.co.in,rmnchadurg@gmail.com | 9425212590 | Dr.rashmi bhonsle | 21-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Poor |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No |  | No | No | Yes | 1 |  | Yes | 1482307964265.jpg | Constant |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | No | No | Yes | Poor
CHC or CH | RAIPUR | DHARSEEVA |  | CHC Birgaon |  | Dr.M.K.Burman | chc.birgaon@gmail.com, cmho_raipur@yahoo.co.in, rmncha2durg@gmail.com | 9425213416 | Mr.Laxman Dhruv | 31-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | Yes | No arrangement for fire safety |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes | No | Yes | 5 |  | Yes | 1482345215123.jpg | Consistently high voltage |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | No proper arrangement for fire prevention
CHC or CH | RAIPUR | TILDA |  | CHC Tilda |  | Dr. A.K. Sinha | bmotilda@yahoo.co.in, cmho_raipur@yahoo.co.in, rmncha2durg@gmail.com | 9753782300 | Dr.A.K.Sinha | 31-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | No arrangement for fire Safety |  | No | Yes | No | No | No | No | No | No |  |  | Yes | No |  | Yes | No | Yes | 10 |  | No |  | Constant |  | No | No | No | Yes | Yes | Yes | No | No | Yes | No | No | No | No | Yes | Yes | No arrangements for fire prevention
DH | RAJNANDGAON |  | DH Rajnandgaon |  |  | Dr | hcrajnandgaon@gmail.com | 7024801789 | Ankita | 28-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | Yes | Yes | No | No |  | No | Yes | No | No | No |  |  |  | No | Na |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Na
PHC | RAJNANDGAON | CHAUKEE |  |  | PHC Jadutola | Sunil yadav | phcjadutola@gmail.com | 9630475833 | Ankita | 20-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Na |  | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No |  | No | No | No |  |  | Yes | 1482228372280.jpg | Constant |  | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | No | No | No | No
PHC | RAJNANDGAON | CHHUIKHADAAN |  |  | PHC Bakar Katta | Lucky | Unlucky26062@gmial.com | 8971546788 | A | 22-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | Yes | No | No |  |  |  | No | Na |  | Yes | Yes | Yes | No | Yes | No | No | Yes | No | Yes | No | No |  | No | No | Yes | 1 |  | No |  | Constant |  | Yes | Yes | Yes | No |  | No | No | Yes | Yes | No | No | No | Yes | No | No | Na
PHC | RAJNANDGAON | CHHUIKHADAAN |  |  | PHC Salhewara | J.mahobia | phcsalhewaea@gmai.com | 9479187584 | A | 22-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No | Na |  | No | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No |  | No | No | No |  |  | Yes | 1482397396835.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | No | Na
PHC | RAJNANDGAON | CHHUIKHADAAN |  |  | PHC Palimeta | Mr.nath | phcpalimeta1984@gmail.com | 9174251519 | A | 22-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Na |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No |  | No | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | No | No | No | No | Nq
CHC or CH | RAJNANDGAON | CHHURIA |  | CHC Chhuria |  | Dr.A.k Basod | bmochuriya@gmail.com | 9424112199 | Ankita | 21-12-2016 |  | Yes | Dry Chemical Powder |  | 21581 | Yes | [10 empty] | No |  | No | Yes | Yes | Yes | Yes | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | Yes | Yes | No | No |  | No | No | No | No | No |  |  |  | No | Na |  | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | No | No |  | No | No | No |  |  | Yes | 1482309060485.jpg | Constant |  | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | No | No | No | No | No | Na
PHC | RAJNANDGAON | CHHURIA |  |  | PHC Khobha | Mr.sunil yadav | Phckhobha@gmail.com | 9421114911 | Ankita | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Na |  | No | Yes | No | No | No | No | No | Yes | Yes | Yes | No | No |  | Yes | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | No |  | No | No | No | No | No | No | No | No | No | No | Nq
PHC | RAJNANDGAON | CHHURIA |  |  | PHC Gainda Tola | Mrs.bais | phcgaindatola@gmail.com | 9412166564 | Ankita | 21-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Na |  | No | No | No | No | No | No | No | No |  |  | No | No |  | No | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Na
PHC | RAJNANDGAON | DONGARGAON |  |  | PHC Tappa | Rashmi petanwar | phctappa@gmail.com | 9993909600 | A | 23-12-2016 |  | No | [21 empty] | Yes | Main door |  | 2 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No | Na |  | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | No | No |  | No | No | No |  |  | Yes | 1482491083651.jpg | Constant |  | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | No | No | No | Na
CHC or CH | RAJNANDGAON | DONGARGARH |  | CHC Dongargarh |  | Dr.B.P Ekka | Bmodgg@yahoo.co.in | 8982691671 | Tamsil javed | 19-12-2016 |  | No | [21 empty] | Yes | Side door |  |  | 1 |  | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | Yes | No | No | No |  | No | Yes | No | No | No |  |  |  | No | Don't have single protocol of fire safety |  | No | No | No | No | No | No | No | Yes | Yes | Yes | No | Yes | Photo therapy | No | Yes | No |  |  | No |  | Constant |  | Yes | Yes | Yes | No |  | No | No | Yes | Yes | No | No | No | Yes | No | No | ..
PHC | RAJNANDGAON | DONGARGARH |  |  | PHC Murmunda | Dr. Limesh Joshi | phcmurmumda@gmail.com | 7828369284 | Tamsil Javed | 19-12-2016 |  | No | [21 empty] | Yes | Side door |  |  | 1 |  | No | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Complete fire safety norms must be provided |  | No | No | No | Yes | No | No | No | Yes | Yes | Yes | No | No |  | No | No | No |  |  | Yes | 1482152073488.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | No | Yes | ..
PHC | RAJNANDGAON | DONGARGARH |  |  | PHC Lalbhadur Nagar | Dr.Navrang | phclbnagar@gmail.com | 9755817611 | Ankita | 23-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Na |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | No | No | No | Na
PHC | RAJNANDGAON | DONGARGARH |  |  | PHC Rama Tola | Mrs jharna agarwal | phcjharna@gmail.com | 8917134611 | A | 23-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | No | No | No |  |  | No |  | No |  |  | Yes | No | Yes | Yes | No | No | No |  | No | No | No | No | No |  |  |  | No | Na |  | Yes | No | Yes | No | Yes | No | No | Yes | Yes | No | No | No |  | No | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | No |  | No | No | No | No | No | No | No | No | No | No | Na
PHC | RAJNANDGAON | DONGARGARH |  |  | PHC Charbhatha | Mr.Dewangan | phccharbhata@gmail.com | 8959974073 | Ankita | 24-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No | Na |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | No | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | No |  | Yes | No | Yes | No | No | No | Yes | Yes | No | Yes | Na
PHC | RAJNANDGAON | KHAIRAGARH |  |  | PHC Jalbandha | Rashmi | rashmilile@gmail.com | 9424115417 | Ankita | 24-12-2016 |  | Yes | Dry Chemical Powder |  | 61 | Yes | [10 empty] | No |  | Yes | Yes | No | No | Yes | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | No | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No | Na |  | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No |  | No | No | No |  |  | No |  | Others | Solar taking load only at few places after power cut | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | No | No | Nw
PHC | RAJNANDGAON | MOHALAA |  |  | PHC Gotatola | Mrr.sunil | phcgotatola@gmial.com | 9424105751 | Ankita | 26-12-2016 |  | No | [21 empty] | No | [5 empty] | Yes | No | No | No |  |  | No |  | No |  |  | No | No | Yes | Yes | No | No | No |  | No | Yes | No | No | No |  |  |  | No | Na |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  | Yes | No | No |  |  | No |  | Constant |  | Yes | Yes | Yes | No |  | Yes | No | No | No | No | No | No | No | No | No | Na
DH | SURAJPUR |  | DH Surajpur |  |  | Dr. Snehlata Tirkey | cmhosurgujagmail.com, rmnchasurguja@gmail.com, | 9826757066 | Mona Arora | 20-12-2016 |  | No | [21 empty] | No | [5 empty] | No | No | No | No |  |  | No |  | No |  |  | No | No | No | No | No | No | No |  | No | No | No | No | No |  |  |  | No | .. |  | No | No | No | No | No | No | No | No |  |  | No | No |  | No | No | No |  |  | Yes | 1482231287871.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | Yes | No | Yes | No | Fire extinguishers n training for fire safety should be given
CHC or CH | SURAJPUR | PRATAPPUR |  | CHC Pratappur |  | Dr.Rajesh Shresth | bmochcpratappur@gmail.com,rmnchabalrampur@gmail.com,cmhosurajpur@gmail.com,naik04@rediffmail.com | 8435300104 | Dr.Pradeep Kr. Gautam | 22-12-2016 |  | No | [21 empty] | Yes | Main door, Side door, Others | Door next to old building is opening at OTS | 1 | 1 | 1 | Yes | Yes | No | No |  |  | No |  | No |  |  | No | Yes | Yes | Yes | No | No | No |  | No | Yes | Yes | No | No |  |  |  | No | Fire extinguisher should be installed |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No |  | No | Yes | No |  |  | Yes | 1482426744456.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | Yes | Yes
PHC | SURAJPUR | PRATAPPUR |  |  | PHC Dharampur | Shri Neeraj Kumar Das | bmochcpratappur@gmail.com,rmnchabalrampur@gmail.com,cmhosurajpur@gmail.com,naik04@gmail.com | 8435300104 | Dr.Pradeep Kr. Gautam | 23-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | Yes | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | No | Yes | Yes | No | No | No | No | Yes | Yes | No | No | No |  | No | No | Yes | 2 |  | No |  | Consistently low voltage |  | Yes | Yes | Yes | No |  | Yes | No | Yes | Yes | No | No | No | No | Yes | Yes
PHC | SURAJPUR | PRATAPPUR |  |  | PHC Pendari | Dr.Umesh Kumar Shukla | bmochcpratappur@gail.com,cmhosurajpur@gmail.com,naik04@rediffmail.com,rmnchabalrampur@gmail.com | 8435300104 | Dr.Pradeep kr.Gautam | 23-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | No | No | No |  | No | No | No | No | No |  |  |  | No | Need to install fire extinguisher |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No | No |  |  | Yes | 1482459771753.jpg | Consistently low voltage |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | No | Yes | Yes
PHC | SURAJPUR | PRATAPPUR |  |  | PHC Ramkola | Shri Narayan Soni | bmochcpratappur@gmail.com,cmhosurajpur@gmail.com,rmnchabalrampur@gmail.com,naik04@gmail.com | 9753059469 | Dr.Pradeep Kr.Gautam | 23-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | No | Yes | No | No |  |  | No |  | No |  |  | No | Yes | Yes | No | No | No | No |  | No | No | No | No | No |  |  |  | No |  |  | No | No | Yes | No | Yes | No | No | Yes | No | No | No | No |  | No | Yes | Yes | 2 |  | Yes | 1482464491103.jpg | Consistently low voltage |  | No | Yes | Yes | No |  | No | No | No | Yes | No | No | No | No | Yes | Yes
CHC or CH | SURAJPUR | PREMNAGAR |  | CHC Premnagar |  | Dr.Brijmohan Kamre | cmhosurajpur@gmail.com,rmnchabalrampur@gmail.com,bmopremnagar@gmail.com,naik04@rediffmail.com | 7828225005 | Dr.Pradeep Kr. Gautam | 23-12-2016 |  | No | [21 empty] | Yes | Main door, Side door |  | 2 | 2 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | Yes | Yes | No | No | No | No |  | No | Yes | Yes | No | No |  |  |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No | No |  |  | Yes | 1482458288418.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | Yes
PHC | SURAJPUR | PREMNAGAR |  |  | PHC Umeshwarpur | Dr.Manoj Kumar Sahu | bmopremnagar@gmail.com,cmhosurajpur@gmail.com,rmnchabalrampur@gmail.com,naik04@rediffmail.com | 8103781688 | Dr.Pradeep kr.Gautam | 23-12-2016 |  | No | [21 empty] | Yes | Main door |  | 1 |  |  | Yes | Yes | No | No |  |  | No |  | No |  |  | Yes | Yes | Yes | No | No | No | No |  | No | Yes | No | No | No |  |  |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No | No |  |  | Yes | 1482464987003.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes
CHC or CH | SURAJPUR | SURAJPUR |  | CHC Bishrampur |  | Dr.Saruta | rmnchabalrampur@gmail.com,cmhosurajpur@gmail.com,bmosurajpur@gmail.com,naik04@rediffmail.com | 9111478286 | Dr.Pradeep Kr. Gautam | 22-12-2016 |  | No | [21 empty] | Yes | Main door, Side door |  | 2 | 1 |  | Yes | Yes | No | No |  |  | No |  | No |  |  | No | Yes | Yes | Yes | No | No | Yes | 6 | No | Yes | Yes | No | No |  |  |  | No | Fire extinguisher should be install in the facility |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No |  | No | Yes | No |  |  | Yes | 1482425866284.jpg | Constant |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | No | No | Yes